## Slim FCU
130mm Slim Exposed Fan Coil Unit
Model | Panel type | LH | AFC-100CO/4A1 | AFC-200CO/4A1 | AFC-300CO/4A1 | AFC-400CO/4A1
Factory Model | Panel type | LH | YG-10（1300RPM) | YG-20（1400RPM) | YG-30（1300RPM) | YG-40（1600RPM)
Power | / | V~,Hz,Ph | 220V,50Hz,1PH | 220V,50Hz,1PH | 220V,50Hz,1PH | 220V,50Hz,1PH
Whole Machine Power | Rated Power | w | 27 | 32 | 35 | 40
| Max Power | w | 50 | 62 | 80 | 80
7℃Cooling Capacity | Max Speed | w | 805 | 1680 | 2700 | 3450
| Hi Speed | w | 680 | 1480 | 2370 | 3080
| Me Speed | w | 570 | 1300 | 1900 | 2560
| Low Speed | w | 500 | 1050 | 1500 | 2150
| Min Speed | w | 430 | 820 | 1100 | 1750
50℃ Heating Capacity | Max Speed | w | 1300 | 2440 | 3400 | 4350
| Hi Speed | w | 1120 | 2130 | 2900 | 3750
| Me Speed | w | 900 | 1730 | 2340 | 3030
| Low Speed | w | 750 | 1450 | 2040 | 2500
| Min Speed | w | 580 | 1200 | 1780 | 2050
70℃ Heating Capacity | Max Speed | w | 2180 | 4140 | 5800 | 7370
| Hi Speed | w | 1800 | 3550 | 4950 | 6340
| Me Speed | w | 1520 | 2930 | 4000 | 5500
| Low Speed | w | 1220 | 2450 | 3230 | 4500
| Min Speed | w | 930 | 2000 | 2580 | 3520
Indoor Fan Motor | Model | / | HDM1089040 | HDM1089040 | HDM1089040 | HDM1089040
| NO | / | 1 | 1 | 1 | 1
| Output Power | w | 27 | 32 | 35 | 40
Indoor Coil | a.Number Of Row |  | 3 | 3 | 3 | 3
| b.Tube Pitch(a)xRow Pitch(b) | mm | 21×12.7 | 21×12.7 | 21×12.7 | 21×12.7
| c.Fin Pitch | mm | 1.2 | 1.2 | 1.2 | 1.2
| d.Fin Material | / | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.And Material | mm | φ7，Inner grooved | φ7，Inner grooved | φ7，Inner grooved | φ7，Inner grooved
| f.Coil LengthxHeightxWidth | mm | 265*294*40 | 455*294*40 | 725*294*40 | 725*294*40
Performance | Air Flow Volume | CFM | 100 | 200 | 300 | 370
|  | m3/h | 170 | 340 | 510 | 630
| Noise Level (sound pressure，max/high/medium/low/min) | dB(A) | 38/37/35/33/32 | 40/39/36/34/33 | 41/40/38/36/35 | 45/44/40/38/37
Water Flow Volume |  | m3/h | 0.18 | 0.3 | 0.5 | 0.6
Hydraulic Resistance |  | Kpa | 16 | 17 | 32 | 50
Max Working pressure |  | Mpa | 1.6 | 1.6 | 1.6 | 1.6
Dimension | Net Dimension (W*D*H) | mm | 757*579*132 | 947*579*132 | 1217*579*132 | 1217*579*132
| Packing Dimension (W*D*H) | mm | 850*690*210 | 1040*690*210 | 1310*690*210 | 1310*690*210
Weight | Net | kg | 16.5 | 19.7 | 24.85 | 24.85
| Gross | kg | 19.0 | 23.0 | 28.0 | 28.0
Drain Pipe |  | mm | DN15 | DN15 | DN15 | DN15
Inlet/Outlet Water Pipe |  | mm | DN20 | DN20 | DN20 | DN20
Remark:The above designs andspecifications aresubject tochange of productimprovement without priornotice.

## Cassette
Specification-Cassette FCU 50HZ
Model |  |  | AFC-300CA/4BA | AFC-400CA/4BA | AFC-500CA/4BA | AFC-600CA/4BA | AFC-800CA/4BA | AFC-1000CA/4BA | AFC-1200CA/4BA | AFC-1400CA/4BA
Factory Model |  |  | 成品AFC-51Ca4/E2 | 成品AFC-68Ca4/E2 | 成品AFC-85Ca4/E2 | 成品AFC-102Ca4/E2 | 成品AFC-136Ca4/E2 | 成品AFC-170Ca4/E2 | 成品AFC-204Ca4/E2 | 成品AFC-238Ca4/E2
Code |  |  | 16117029000010 | 16117029000011 | 16117029000012 | 16117029000013 | 16117029000014 | 16117029000015 | 16117029000016 | 16117029000017
Power |  | V~,Hz,Ph | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1
Air Flow Volume | H/M/L Speed | CFM | 300/259/212 | 400/341/282 | 500/429/353 | 600/450/300 | 800/600/400 | 1000/750/500 | 1200/900/600 | 1400/1050/700
| H/M/L Speed | m3/h | 510/440/360 | 680/580/480 | 850/730/600 | 1020/765/510 | 1360/1020/680 | 1700/1275/850 | 2040/1530/1020 | 2380/1785/1190
Cooling Capacity | H/M/L Speed | w | 3300/2840/2380 | 3900/3350/2810 | 4500/3600/3060 | 5406/4595/3514 | 7210/6129/4687 | 9018/7665/5862 | 10810/9189/7027 | 12611/10719/8197
Heating Capacity | H/M/L Speed | w | 4800/4200/3700 | 5800/5100/4500 | 6750/5940/5200 | 8115/6898/5275 | 10807/9186/7025 | 13512/11485/8783 | 16250/13774/10553 | 18901/16066/12286
Indoor Fan Motor | Model | / | Low noise 3-speed fan motor (XD30B) | Low noise 3-speed fan motor(XD30B) | Low noise 3-speed fan motor (XD30B) | Low noise 3-speed fan motor ( XD30A) | Low noise 3-speed fan motor (YDK35-6Q) | Low noise 3-speed fan motor ( XD80A) | Low noise 3-speed fan motor ( XD80A) | Low noise 3-speed fan motor ( XD80A)
| Number of Fan Motor | / | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Output Power | W | 55 | 62 | 76 | 96 | 134 | 165 | 189 | 225
| Capacitor | uF | 1.5 | 2.0 | 2.5 | 3.0 | 4 | 6 | 6 | 6
Indoor Fan | Number of Fan |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Type |  | Centrifugal wind wheel (White material)
Indoor Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Pitch | mm | 1.5 | 1.5 | 1.5 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| d.Fin Material |  | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 1322*205*25.4 | 1322*205*25.4 | 1322*205*25.4 | 2044*205*25.4 | 2044*205*25.4 | 2044*246*25.4 | 2044*246*25.4 | 2044*246*25.4
Noise Level |  | dB(A) | ≤39 | ≤42 | ≤45 | ≤45 | ≤46 | ≤48 | ≤50 | ≤52
Water Flow Volume |  | m3/h | 0.62 | 0.7 | 0.94 | 1.15 | 1.4 | 1.68 | 1.82 | 2.25
Hydraulic Resistance |  | Kpa | 26 | 27 | 29 | 31 | 34 | 36 | 39 | 42
Max.Working pressure |  | Mpa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
Dimension (W*D*H) | Net Dimension (body) | mm | 570×570×260 | 570×570×260 | 570×570×260 | 835×835×250 | 835×835×250 | 835×835×290 | 835×835×290 | 835×835×290
| Packing Dimension(body) | mm | 650×650×290 | 650×650×290 | 650×650×290 | 910×910×310 | 910×910×310 | 910×910×350 | 910×910×350 | 910×910×350
| Net Dimension (Panel) | mm | 650×650×55 | 650×650×55 | 650×650×55 | 950×950×55 | 950x950x55 | 950x950x55 | 950x950x55 | 950x950x55
| Packing Dimension (Panel) | mm | 710×710×80 | 710×710×80 | 710×710×80 | 1000×1000×100 | 1000x1000x100 | 1000x1000x100 | 1000x1000x100 | 1000x1000x100
Weight | Panel Net/Gross | kg | 3/5 | 3/5 | 3/5 | 5/7 | 5/7 | 5/7 | 5/7 | 5/7
| Body Net/Gross | kg | 18/20.3 | 18/20.3 | 18/20.3 | 24.5/28 | 25.5/29 | 26.5/31 | 28/32.5 | 28/32.5
Drain Pipe（O.D） |  | mm | 16 | 16 | 16 | 30 | 30 | 30 | 30 | 30
Inlet/Outlet Water Pipe(FCU) |  | mm | Rc3/4"(internal thread) | Rc3/4"(internal thread) | Rc3/4"(internal thread) | Rc3/4"(internal thread) | Rc3/4"(internal thread) | Rc3/4"(internal thread) | Rc3/4"(internal thread) | Rc3/4"(internal thread)
Wiring specification | Power Wiring（FCU） | mm2 | 3×1 | 3×1 | 3×1 | 3×1 | 3×1 | 3×1 | 3×1 | 3×1
Stuffing Quantity | 20/40/40H | unit
Remark:The above designs and specifications are subject to change of product improvement without prior notice.
R:British Standard Pipe Taper External Thread
Rc：British Standard Pipe Taper Internal Thread
G：British Standard Pipe Parallel Thread

## wall-mounted（Q）
Specification-Wall Mounted FCU 50HZ
Model | Panel type | LH | AFC-200WM/4A(Q*)-N | AFC-200WM/4A1(Q*)-N | AFC-300WM/4A(Q*)-N | AFC-300WM/4A1(Q*)-N | AFC-400WM/4A(Q*)-N | AFC-400WM/4A1(Q*)-N | AFC-500WM/4A(Q*)-N | AFC-500WM/4A1(Q*)-N | AFC-600WM/4A(Q*)-N | AFC-600WM/4A1(Q*)-N
Factory Model | Panel type | LH | AFC-34W/QC | AFC-34W/QC | AFC-51W/QC | AFC-51W/QC | AFC-68W/QC | AFC-68W/QC | AFC-85W/QC | AFC-85W/QC | AFC-102W/QC | AFC-102W/QC
Code | Panel type | LH | 16117030000010 | 16117030000010 | 16117030000011 | 16117030000011 | 16117030000012 | 16117030000012 | 16117030000013 | 16117030000013 | 16117030000014 | 16117030000014
Power |  | V~,Hz,Ph | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1 | 220-240V,50,1
Whole Machine Power | Rated Power | w | 16 | 16 | 22 | 22 | 44 | 44 | 35 | 35 | 48 | 48
| Max Power | w | 17.6 | 17.6 | 24.2 | 24.2 | 48.4 | 48.4 | 38.5 | 38.5 | 52.8 | 52.8
Cooling Capacity | Max Speed | w | 2700 | 2700 | 2910 | 2910 | 3810 | 3810 | 4514 | 4470 | 5406 | 4900
| Hi Speed | w | 2312 | 2312 | 2312 | 2312 | 3617 | 3617 | 4015 | 3980 | 4940 | 4452
| Me Speed | w | 2015 | 2015 | 2015 | 2015 | 2991 | 2991 | 3514 | 3452 | 4320 | 3822
| Low Speed | w | 1763 | 1763 | 1763 | 1763 | 2609 | 2609 | 3045 | 2965 | 3612 | 3258
45℃Heating Capacity | Max Speed | w | / | 2940 | / | 3230 | / | 4300 | / | 4840 | / | 5260
| Hi Speed | w | / | 2709 | / | 2709 | / | 3671 | / | 4173 | / | 4663
| Me Speed | w | / | 2303 | / | 2303 | / | 2960 | / | 3342 | / | 3967
| Low Speed | w | / | 1761 | / | 1761 | / | 2589 | / | 2909 | / | 3494
60℃Heating Capacity | Max Speed | w | 3500 | / | 4070 | / | 5418 | / | 6767 | / | 8155 | /
| Hi Speed | w | 3409 | / | 3409 | / | 5240 | / | 6125 | / | 7463 | /
| Me Speed | w | 3003 | / | 3003 | / | 4628 | / | 5269 | / | 6577 | /
| Low Speed | w | 2761 | / | 2761 | / | 4014 | / | 4592 | / | 5542 | /
Indoor Fan Motor | Model | / | D-310-30-80A AL | D-310-30-80A AL | D-310-30-80A AL | D-310-30-80A AL | D-310-30-80A AL | D-310-30-80A AL | D-310-50-10A AL | D-310-50-10A AL | D-310-50-10A AL | D-310-50-10A AL
| NO. | / | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Output Power | W | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 50 | 50 | 50
Indoor Coil | a.Number Of Row |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| b.Tube Pitch(a)x Row Pitch(b) | mm | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7 | 20.5×12.7
| c.Fin Pitch | mm | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| d.Fin Material | / | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin | Hydrophilic aluminum fin
| e.Tube Outside Dia.And Material | mm | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved | φ7， Inner grooved
| f.Coil Length x Height x Width | mm | 570*327.5*25.4 | 570*327.5*25.4 | 570*327.5*25.4 | 570*327.5*25.4 | 570*327.5*25.4 | 570*327.5*25.4 | 700*366.8*25.4 | 700*366.8*25.4 | 700*366.8*25.4 | 700*366.8*25.4
Performance | Air Flow Volume | CFM | 289/238/211/186 | 289/238/211/186 | 344/238/211/186 | 344/238/211/186 | 485/396/309/264 | 485/396/309/264 | 507/384/335/294 | 507/384/335/294 | 600/489/418/341 | 600/489/418/341
|  | m3/h | 492/404/358/316 | 492/404/358/316 | 585/404/358/316 | 585/404/358/316 | 825/673/526/448 | 825/673/526/448 | 862/653/570/500 | 862/653/570/500 | 1020/832/710/580 | 1020/832/710/580
| Noise Level（sound pressure，high speed） | dB(A) | 32/26/24 | 32/26/24 | 32/26/24 | 32/26/24 | 44/39/33 | 44/39/33 | 38/34/31 | 38/34/31 | 44/42/36 | 44/42/36
Water Flow Volume |  | m3/h | 0.5 | 0.5 | 0.57 | 0.57 | 0.77 | 0.77 | 0.84 | 0.84 | 0.97 | 0.97
Hydraulic Resistance |  | Kpa | 31.61 | 31.61 | 37.2 | 37.2 | 56.75 | 56.75 | 41.2 | 41.2 | 50.7 | 50.7
Max.Working pressure |  | Mpa | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
Dimension | Net Dimension (W*D*H) | mm | 965*325*230 | 965*325*230 | 965*325*230 | 965*325*230 | 965*325*230 | 965*325*230 | 1089*328*227 | 1089*328*227 | 1089*328*227 | 1089*328*227
| Packing Dimension (W*D*H) | mm | 1020×375×305 | 1020×375×305 | 1020×375×305 | 1020×375×305 | 1020×375×305 | 1020×375×305 | 1155×397×312 | 1155×397×312 | 1155×397×312 | 1155×397×312
Weight | Net | kg | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 13.5 | 13.5 | 13.5 | 13.5
| Gross | kg | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 16.5 | 16.5 | 16.5 | 16.5
Drain Pipe(O.D) |  | mm | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 16.9
Inlet/Outlet Water Pipe(FCU) |  | mm | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread ) | G3/4"(internal thread )
Stuffing Quantity | 20/40/40H | unit | 253/526/608 | 253/526/608 | 253/526/608 | 253/526/608 | 253/526/608 | 253/526/608 | 216/438/498 | 216/438/498 | 216/438/498 | 216/438/498
Remark:The above designs and specifications are subject to change of product improvement without prior notice.
R:British Standard Pipe Taper External Thread
Rc：British Standard Pipe Taper Internal Thread
G：British Standard Pipe Parallel Thread